{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":35,"n_cols":8,"rows_kept":35,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","3MXM-A"]
[]
[]
[]
[]
["","","","","","3MXM40A2V1B","3MXM52A2V1B","3MXM68A2V1B"]
["Mål","Enhed","","Højde","mm","734","734","734"]
["","","","Bredde","mm","974","974","974"]
["","","","Dybde","mm","408","408","408"]
["Vægt","Enhed","","","kg","57","57","62"]
["Kompressor","Type","","","","Hermetisk lukket svingkompressor","Hermetisk lukket svingkompressor","Hermetisk lukket svingkompressor"]
["Driftsområde","Køle","Omgivende","Min.","°CDB","-10","-10","-10"]
["","","","Max.","°CDB","46","46","46"]
["Lydtryk","Køle","","Nom.","dBA","46","46","48"]
["","Varme","","Nom.","dBA","47","47","48"]
["Kølemiddel","Type","","","","R-32","R-32","R-32"]
["","Belastning","","","kg","1.8","1.8","2"]
["","Påfyldning","","","tCO2Eq","1.22","1.22","1.35"]
["","GWP","","","","675","675","675"]
["Rørtilslutninger","Rørlængde","Max.","OU - IU","m","25 (1)","25","25 (1)"]
["","Ekstra kølemiddelopladning","","","kg/m","0,02 (til rørlængde over 30 m)","0,02 (til rørlængde over 30 m)","0,02 (til rørlængde over 30 m)"]
["","Niveauforskel","IU - OU","Max.","m","15","15","15"]
["","","IU - IU","Max.","m","7.5","7.5","7.5"]
["","Samlet rørlængde","System","Nuværende","m","50 (2)","50","50"]
["Standardtilbehør","Installation manual","","","","1","1","1"]
["","Drain cap","","","","3","3","3"]
["","Drain plug","","","","1","1","1"]
["","Reducer assembly","","","","1","1","1"]
["","Screw bag","","","","1","1","1"]
["Strømforsyning","Fase","","","","1~","1~","1~"]
["","Frekvens","","","Hz","50","50","50"]
["","Strømspænding","","","V","220-240","220-240","220-240"]
["Bemærkninger","","","","","(1) - Til ét rum","(1) - Til ét rum"]
["","","","","","(2) - Til kombination med CVXM-A, FVXM-A - maksimal rørlængde er 30 m.","(2) - Til kombination med CVXM-A, FVXM-A - maksimal rørlængde er 30 m."]
["","","","","","","","(1) - Til ét rum"]