{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":57,"n_cols":16,"rows_kept":57,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","EWFS-TZXSD"]
[]
[]
[]
[]
["","","","","","","EWFSH11TZXSD2","EWFSH10TZXSD2","EWFSC10TZXSD2","EWFSH12TZXSD2","EWFSC12TZXSD2","EWFSH13TZXSD2","EWFSH14TZXSD2","EWFSH15TZXSD2","EWFSH16TZXSD2","EWFSH17TZXSD2"]
["Kølekapacitet","Nom.","","","","kW","1436.39","1370.23","1274.13","1603.58","1536.75","1720.07","1866.66","1957.89","2092.93","2138.76"]
["Kapacitetsstyring","Metode","","","","","","Trinløs","Trinløs","Trinløs","Trinløs","Trinløs","Trinløs","Trinløs","Trinløs","Trinløs"]
["Kapacitetsstyring","Minimumskapacitet","","","","%","10.5","10.5","11.5","10","10","10","15","13.5","12.5","11.5"]
["Indgangseffekt","Køle","","","Nom.","kW","405.88","407.56","356.3","489.2","463.58","532.36","523.31","577.55","655.27","711.26"]
["EER","","","","","","3.54","3.36","3.58","3.28","3.32","3.23","3.57","3.39","3.19","3.01"]
["IPLV","","","","","","5.764","5.84","5.977","5.541","5.622","5.84","6.097","5.958","6.475","6.196"]
["SEER","","","","","","5.793","4.899","5.183","5.627","5.68","5.687","5.603","5.478","5.355","5.225"]
["Mål","Enhed","","","Dybde","mm","11200","10120","10120","11200","11200","12280","13360","13360","13360","13360"]
["","","","","Højde","mm","2553","2553","2553","2553","2553","2553","2553","2553","2553","2553"]
["","","","","Bredde","mm","2238","2238","2238","2238","2238","2238","2238","2238","2238","2238"]
["Vægt","Driftsvægt","","","","kg","9391","8619","8609","9416","9401","10826","12080","12095","12110","12125"]
["Vægt","Enhed","","","","kg","","7390","7390","8011","8011","8892","10070","10070","10070","10070"]
["Kabinet","Farve","","","","","","Elfenbenshvid","Elfenbenshvid","Elfenbenshvid","Elfenbenshvid","Elfenbenshvid","Elfenbenshvid","Elfenbenshvid","Elfenbenshvid","Elfenbenshvid"]
["Kabinet","Materiale","","","","","Galvaniseret og malet stålplade","Galvaniseret og malet stålplade","Galvaniseret og malet stålplade","Galvaniseret og malet stålplade","Galvaniseret og malet stålplade","Galvaniseret og malet stålplade","Galvaniseret og malet stålplade","Galvaniseret og malet stålplade","Galvaniseret og malet stålplade","Galvaniseret og malet stålplade"]
["Vandvarmeveksler - fordamper","Type","","","","","Skal og slange","Skal og slange","Skal og slange","Skal og slange","Skal og slange","Skal og slange","Skal og slange","Skal og slange","Skal og slange","Skal og slange"]
["","Vandmængde","","","","l","557","481","481","557","557","1011","1011","1011","1011","1011"]
["","Fald i vandtryk","","Køling","Nom.","kPa","49.11","50.08","44.79","35.27","54.41","39.09","43.42","46.69","51.88","53.91"]
["Luftvarmeveksler","Type","","","","","Mikrokanal","Mikrokanal","Mikrokanal","Mikrokanal","Mikrokanal","Mikrokanal","Mikrokanal","Mikrokanal","Mikrokanal","Mikrokanal"]
["Ventilator","Mængde","","","","","20","18","18","20","20","22","24","24","24","24"]
["","Type","","","","","Popeller med direkte drev","Popeller med direkte drev","Popeller med direkte drev","Popeller med direkte drev","Popeller med direkte drev","Popeller med direkte drev","Popeller med direkte drev","Popeller med direkte drev","Popeller med direkte drev","Popeller med direkte drev"]
["","Luftmængde","","Køle","Nom.","l/sek","112550","101295","101295","112550","112550","123805","135060","135060","135060","135060"]
["Ventilatormotor","Drev","","","","","Uden børste","Uden børste","Uden børste","Uden børste","Uden børste","Uden børste","Uden børste","Uden børste","Uden børste","Uden børste"]
["Kompressor","Mængde_","","","","","2","2","2","2","2","2","2","2","2","2"]
["Kompressor","Type","","","","","","Skruekompressor","Skruekompressor","Skruekompressor","Skruekompressor","Skruekompressor","Skruekompressor","Skruekompressor","Skruekompressor","Skruekompressor"]
["Driftsområde","Luftside","","Køle","Min.","°CDB","4","4","4","4","4","4","4","4","4","4"]
["","","","","Max.","°CDB","18","18","18","18","18","18","18","18","18","18"]
["","Vandside","","Driftsområde-=-Vandside-=-Køle","Driftsområde-=-Vandside-=-Køle-=-Min.-=-°CDB","°CDB","","5","5","5","5","5","5","5","5","5"]
["","","","","Driftsområde-=-Vandside-=-Køle-=-Max.-=-°CDB","°CDB","","42","42","42","42","42","42","42","42","42"]
["Lydeffektniveau","Køle","","","Nom.","dBA","103","102.3","101","107.5","105.2","106.1","102","102.8","103.7","104.5"]
["Lydtryk","Køle","","","Nom.","dBA","77.6","77.5","76.8","78","77.9","79.1","78.9","79.7","80.5","81.4"]
["Kølemiddel","Type","","","","","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A","R-513A"]
["Kølemiddel","GWP","","","","","","630","630","630","630","630","630","630","630","630"]
["Kølemiddel","Kølemiddel-=-Opladning-=-kg","","","","kg","","145","135","180","165","190","200","215","230","245"]
["","Kredsløb","","","Mængde","","2","2","2","2","2","2","2","2","2","2"]
["Rørtilslutninger","Fordamper vandtilgang/-afløb (UD)","","","","","","219.1","219.1","219.1","219.1","273","273","273","273","273"]
["Strømforsyning","Fase","","","","","3","3","3","3","3","3","3","3","3","3"]
["","Strømforsyning-=-Frekvens","","","Frekvens","","50","50","50","50","50","50","50","50","50","50"]
["","Strømforsyning-=-Strømspænding","","","Strømspænding","","400","400","400","400","400","400","400","400","400","400"]
["","Strømspændingsområde","","Min.","Min.","","-10","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Strømforsyning-=-Strømspændingsområde-=-Max.","Max.","","10","10","10","10","10","10","10","10","10","10"]
["Enhed","Startstrøm","","Enhed-=-Startstrøm-=-Maks.","Maks.","","0","0","0","0","0","0","0","0","0","0"]
["","Driftsstrøm","Køle","Enhed-=-Driftsstrøm-=-Køle-=-Nom.","Nom.","","645","648","572","769","731","833","828","909","1024","1115"]
["","","","Enhed-=-Driftsstrøm-=-Maks.","Maks.","","744","782","720","851","803","899","997","1103","1217","1330"]
["","Enhed-=-Max. enhedsstrøm til ledningernes størrelse","","","Max. enhedsstrøm til ledningernes størrelse","","819","860","792","924","883","924","1097","1214","1268","1463"]
["Kapacitetsstyring","Metode","","","","","Trinløs"]
["Vægt","Enhed","","","","kg","8011"]
["Kabinet","Farve","","","","","Elfenbenshvid"]
["Kompressor","Type","","","","","Skruekompressor"]
["Kølemiddel","GWP","","","","","630"]
["","Belastning","","","","kg","155"]
["Rørtilslutninger","Fordamper vandtilgang/-afløb (UD)","","","","","219.1"]