{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":44,"n_cols":6,"rows_kept":44,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWC-DF"]
[]
[]
[]
[]
["","","","","","FWC07DAFN5V3--"]
["Kølekapacitet (standard betingelser)","Sensibel kapacitet 4-rørs","","Lav","kW","3.26"]
["","","","Høj","kW","5.58"]
["","Samlet kapacitet 4-rørs","","Lav","kW","4.35"]
["","","","Høj","kW","7.15"]
["Varmekapacitet (standard betingelser)","Kapacitet 4-rørs","","Lav","kW","5.34"]
["","","","Høj","kW","8.82"]
["Strømforbrug","Lav","","","kW","0.02"]
["","Høj","","","kW","0.069"]
["Mål","Enhed","","Højde","mm","287"]
["","","","Bredde","mm","837"]
["","","","Dybde","mm","921"]
["Vægt","Enhed","","","kg","27"]
["Ventilator","Luftmængde","","Lav","m³/t","686"]
["","","","Høj","m³/t","1296"]
["Totalt lydtryksniveau","Lav","","","dBA","36"]
["","Høj","","","dBA","52"]
["Lydtryk","Lav","","","dBA","23"]
["","Høj","","","dBA","39"]
["Vandflow","Køling","","Lav","l/t","776"]
["","","","Høj","l/t","1295"]
["","Opvarmning","","Lav","l/t","459"]
["","","","Høj","l/t","759"]
["","Fald i vandtryk","Køling","Lav","kPa","13"]
["","","","Høj","kPa","25"]
["","","Opvarmning","Lav","kPa","13"]
["","","","Høj","kPa","24"]
["Rørtilslutninger","Vand","","Indgang","","3/4\" BSP (hungevind)"]
["","","","Udledning","","3/4\" BSP (hungevind)"]
["","Dræn","","UD","mm","VP25 (ekstern dia.32; intern dia. 25)"]
["Strømforsyning","Strømforsyning-=-Type","","","","230 / 1 / 50"]
["","Fase","","","","1~"]
["","Frekvens","","","Hz","50"]
["","Strømspænding","","","V","230"]
["Bemærkninger","","","","","(1) - Køling: luft 27 °CDB, 19°CWB; indgående vand 7 °C; udgående vand 12°C"]
["","","","","","(2) - Opvarmning: 2 rør: luft 20°CDB, 15°CWB; indgående vand 45° C; udgående vand 40° C"]
["","","","","","(3) - Opvarmning: 4 rør: luft 20°CDB, 15°CWB; indgående vand 65° C; udgående vand 55° C"]
["","","","","","(4) - Før ikke vand på mindre end 5°C eller mere end 90°C ind i enheden, da det kan skade enheden"]
["","","","","","(5) - Luftflow: 20 °C DB, 15 °C WB; 230 V 50 Hz 0 Pa"]