{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":69,"n_cols":8,"rows_kept":69,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","FWXM-ATV3R"]
[]
[]
[]
[]
["","","","","","FWXM10AATV3R","FWXM15AATV3R","FWXM20AATV3R"]
["Kølekapacitet","7/12°C","","Min.","kW","0.75","1.15","1.32"]
["","","","Mid.","kW","1.36","2.08","2.39"]
["","","","Maks.","kW","2.12","2.81","3.30"]
["Sensibel kølekapacitet","7/12°C","","Min.","kW","0.59","0.83","1.02"]
["","","","Mid.","kW","1.04","1.51","1.84"]
["","","","Maks.","kW","1.54","2.11","2.65"]
["Varmekapacitet","45/40°C","","Min.","kW","0.82","1.20","1.47"]
["","","","Mid.","kW","1.53","2.16","2.59"]
["","","","Maks.","kW","2.21","3.02","3.81"]
["Strømforbrug","Min.","","","kW","0","0.01","0.01"]
["","Mid.","","","kW","0.01","0.01","0.01"]
["","Maks.","","","kW","0.02","0.02","0.03"]
["Ventilatorhastighed","Min.","","","o/min","680.00","680.00","680.00"]
["","Mid.","","","o/min","1100.00","1100.00","1100.00"]
["","Maks.","","","o/min","1500.00","1500.00","1500.00"]
["Kabinet","Farve","","","","indbygget","indbygget","indbygget"]
["","Materiale","","","","Intet kabinet","Intet kabinet","Intet kabinet"]
["Mål","Enhed","","Højde","mm","576","576","576"]
["","","","Bredde","mm","725","925","1125"]
["","","","Dybde","mm","126","126","126"]
["","Pakket enhed","","Højde","mm","690","690","690"]
["","","","Bredde","mm","830","1030","1230"]
["","","","Dybde","mm","210","210","210"]
["Vægt","Enhed","","","kg","12","15","18"]
["","Pakket enhed","","","kg","13","16","19"]
["Pakke","Materiale","","","","Karton","Karton","Karton"]
["","Vægt","","","kg","1","1","1"]
["Varmeveksler","Mængde","","","","1","1","1"]
["","Intern spolevolumen","","","l","0.8","1.13","1.46"]
["","Påfyldning","","Driftstryk","bar","10","10","10"]
["Vandkredsløb","Rørtilslutningers diameter","","","in","3/4","3/4","3/4"]
["","Rørføringsmateriel","","","","KOBBER","KOBBER","KOBBER"]
["","Tryk","Opvarmning","Maks.","bar","10","10","10"]
["Vandkreds - fald i vandtryk","Opvarmning","45/40°C","Min.","kPa","1.50","2.70","3.00"]
["","","","Mid.","kPa","4.30","9.30","8.90"]
["","","","Maks.","kPa","9.20","19.10","21.20"]
["","Køling","7/12°C","Min.","kPa","1.90","2.70","2.50"]
["","","","Mid.","kPa","4.30","9.90","8.80"]
["","","","Maks.","kPa","8.20","17.10","18.00"]
["Vandkreds - vandstrømshastighed","Opvarmning","45/40°C","Min.","kg/t","140.00","210.00","260.00"]
["","","","Mid.","kg/t","270.00","380.00","450.00"]
["","","","Maks.","kg/t","390.00","530.00","660.00"]
["","Køling","7/12°C","Min.","kg/t","130.00","200.00","230.00"]
["","","","Mid.","kg/t","230.00","360.00","410.00"]
["","","","Maks.","kg/t","360.00","480.00","570.00"]
["Lydeffektniveau","Min.","","","dBA","35","36","36"]
["","Mid.","","","dBA","45","46","47"]
["","Maks.","","","dBA","53.0","54.0","55.0"]
["Driftsområde","Varme","Vandside","Min.","°C","30","30","30"]
["","","","Max.","°C","85","85","85"]
["","Køle","Vandside","Min.","°C","5","5","5"]
["","","","Max.","°C","18","18","18"]
["","Indendørs installation","Omgivende","Min.","°CDB","0","0","0"]
["","","","Maks.","°CDB","45","45","45"]
["Styresystemer","Trådløs fjernbetjening","","","","Nej","Nej","Nej"]
["","Integreret på indendørs enhed","","","","Ja","Ja","Ja"]
["Strømforsyning","Fase","","","","1~","1~","1~"]
["","Frekvens","","","Hz","50","50","50"]
["","Strømspænding","","","V","230","230","230"]
["Elforbrug","Maks.","","","W","19","20","29"]
["","Standby","","","W","3","4","5"]
["Effekt","Maksimal driftsstrøm","","Varme","A","0.16","0.18","0.26"]
["Strøm","Maks. driftsstrøm","","Køling","A","0.16","0.18","0.26"]