{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":31,"n_cols":14,"rows_kept":31,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXP-M"]
[]
[]
[]
[]
["","","","","","RXP20M5V1B","RXP25M5V1B","RXP35M5V1B","RXP50M2V1B","RXP50M5V1B","RXP60M2V1B","RXP60M5V1B","RXP71M2V1B","RXP71M5V1B"]
["Mål","Enhed","","Højde","mm","550","550","550","734","734","734","734","734","734"]
["","","","Bredde","mm","658","658","658","870","870","870","870","870","870"]
["","","","Dybde","mm","275","275","275","373","373","373","373","373","373"]
["Vægt","Enhed","","","kg","26","26","28","46.0","46.0","50.0","50.0","50.0","50.0"]
["Kompressor","Type","","","","Hermetisk lukket svingkompressor","Hermetisk lukket svingkompressor","Hermetisk lukket svingkompressor","Hermetisk lukket svingkompressor","Hermetisk lukket svingkompressor","Hermetisk lukket svingkompressor","Hermetisk lukket svingkompressor","Hermetisk lukket svingkompressor","Hermetisk lukket svingkompressor"]
["Driftsområde","Køle","Omgivende","Min.","°CDB","-10","-10","-10","-10","-10","-10","-10","-10","-10"]
["","","","Max.","°CDB","48","48","48","46","48","46","48","46","48"]
["Lydtryk","Køle","","Nom.","dBA","46","46","48","47","47","49","49","52","52"]
["","Varme","","Nom.","dBA","47","47","48","49","49","49","49","52","52"]
["Kølemiddel","Type","","","","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32","R-32"]
["","Belastning","","","kg","0.55","0.55","0.70","0.90","0.90","1.15","1.15","1.15","1.15"]
["","Påfyldning","","","tCO2Eq","0.37","0.37","0.48","0.61","0.61","0.78","0.78","0.78","0.78"]
["","GWP","","","","675.0","675.0","675.0","675","675","675","675","675","675"]
["Rørtilslutninger","Rørlængde","Max.","OU - IU","m","15","15","15","30","30","30","30","30","30"]
["","Ekstra kølemiddelopladning","","","kg/m","0,02 (til rørlængde over 10 m)","0,02 (til rørlængde over 10 m)","0,02 (til rørlængde over 10 m)","0,02 (til rørlængde over 10 m)","0,02 (til rørlængde over 10 m)","0,02 (til rørlængde over 10 m)","0,02 (til rørlængde over 10 m)","0,02 (til rørlængde over 10 m)","0,02 (til rørlængde over 10 m)"]
["","Niveauforskel","IU - OU","Max.","m","12","12","12","20","20","20","20","20","20"]
["Standardtilbehør","Installation manual","","","","1","1","1","1","1","1","1","1","1"]
["","Refrigerant charge label","","","","1","1","1","1","1","1","1","1","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1","1","1","1","1","1","1","1","1"]
["","Drain cap","","","","","","","3","3","3","3","3","3"]
["","Drain plug","","","","1","1","1","1","1","1","1","1","1"]
["Strømforsyning","Fase","","","","1~","1~","1~","1~","1~","1~","1~","1~","1~"]
["","Frekvens","","","Hz","50","50","50","50","50","50","50","50","50"]
["","Strømspænding","","","V","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240","220-240"]
["Standardtilbehør","General safety precautions","","","","1","1","1"]