{"text_format":"2","workbook":"xls","n_sheets":1,"sheets":["Products"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":1,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Products","index":0,"n_rows":72,"n_cols":8,"rows_kept":72,"cut":false,"hidden":false,"merged":[],"flags":["formulas_cached_only"]}
["PRODUCT NAME","RXS-L3"]
[]
[]
[]
[]
["","","","","","RXS20L3V1B","RXS25L3V1B","RXS35L3V1B"]
["Lydtryk","Varme","","Høj","dBA","","","48"]
["","Køle","","Høj","dBA","","","48"]
["Standardtilbehør","Installationsvejledning","","","","","","1"]
["","Mærkat for kølemiddelmængde","","","","","","1"]
["","Flersproget mærkat for fluorholdige drivhusgasser","","","","","","1"]
["","Afløbsprop (kun varmepumpemodeller)","","","","","","1"]
["Kølemiddel","Charge","","","TCO2Eq","","","2.5"]
["","GWP","","","","","","2,087.5"]
["","Opladning","","","kg","","","1.2"]
["","Type","","","","","","R-410A"]
["Ventilatormotor","Hastighed","Køle","Super lav","o/min","","","780"]
["","","Varme","Super lav","o/min","","","740"]
["Driftsområde","Køle","Omgivende","Max.","°CDB","","","46"]
["","","","Min.","°CDB","","","-10"]
["","Varme","Omgivende","Max.","°CWB","","","18"]
["","","","Min.","°CWB","","","-15"]
["Rørtilslutninger","Niveauforskel","IU - OU","Max.","m","","","15"]
["","Ekstra kølemiddelopladning","","","kg/m","","","0,02 (til rørlængde over 10 m)"]
["Mål","Unit","","Width","mm","","","765"]
["","","","Depth","mm","","","285"]
["","","","Height","mm","","","550"]
["Kompressor","Type","","","","","","Hermetisk lukket svingkompressor"]
["Vægt","Unit","","","kg","","","34"]
["Ventilator","Luftmængde","Varme","Super lav","cfm","","","904"]
["","","","Super lav","m³/min","","","25.6"]
["","","Køle","Super lav","m³/min","","","30.1"]
["","","","Super lav","cfm","","","1,063"]
["Power supply","Fase","","","","","","1~"]
["","Frekvens","","","Hz","","","50"]
["","Strømspænding","","","V","","","220-240"]
["Bemærkninger","","","","","","","(1) - SL: Luftstrømmens hastighedsindstillings lydløse ventilatorniveau"]
["Ventilator","Luftmængde","Køle","Super lav","m³/min","30.1","30.1"]
["","","Varme","Super lav","m³/min","25.6","25.6"]
["","","","Super lav","cfm","1063","1063"]
["","","Varme","Super lav","cfm","904","904"]
["Mål","Enhed","","Højde","mm","550","550"]
["","","","Bredde","mm","765","765"]
["","","","Dybde","mm","285","285"]
["Vægt","Enhed","","","kg","34","34"]
["Ventilatormotor","Hastighed","Køle","Super lav","o/min","780","780"]
["","","Varme","Super lav","o/min","740","740"]
["Kompressor","Type","","","","Hermetisk lukket svingkompressor","Hermetisk lukket svingkompressor"]
["Driftsområde","Køle","Omgivende","Min.","°CDB","-10","-10"]
["","","","Max.","°CDB","46","46"]
["","Varme","Omgivende","Min.","°CWB","-15","-15"]
["","","","Max.","°CWB","18","18"]
["Lydtryk","Køle","","Høj","dBA","46","46"]
["","Varme","","Høj","dBA","47","47"]
["Kølemiddel","Type","","","","R-410A","R-410A"]
["","Belastning","","","kg","1.0","1.0"]
["","Påfyldning","","","tCO2Eq","2.1","2.1"]
["","GWP","","","","2087.5","2087.5"]
["Rørtilslutninger","Rørlængde","Max.","OU - IU","m","20","20"]
["","Ekstra kølemiddelopladning","","","kg/m","0,02 (til rørlængde over 10 m)","0,02 (til rørlængde over 10 m)"]
["","Niveauforskel","IU - OU","Max.","m","15","15"]
["Standardtilbehør","Installation manual","","","","1","1"]
["","Refrigerant charge label","","","","1","1"]
["","Multilingual fluorinated greenhouse gases labels","","","","1","1"]
["","Drain plug","","","","1"]
["Strømforsyning","Fase","","","","1~","1~"]
["","Frekvens","","","Hz","50","50"]
["","Strømspænding","","","V","220-240","220-240"]
["Bemærkninger","","","","","(1) - 220V"]
["","","","","","(2) - 230V"]
["","","","","","(3) - 240V"]
["Standardtilbehør","Drain plug (only heat pump models)","","","","","1"]